## 00_README
KPTCL DSU — Master Data V8
Decision Support Unit · Index & Data Collection Guide
Purpose | This workbook is the single source of truth feeding the KPTCL DSU dashboard (dsu_dashboard.html). Every figure currently simulated/hardcoded in the live tool is listed here by sheet, ready for you to replace with verified historical and live data from KPTCL/ESCOM systems.
Legend
Blue text | Placeholder / assumption value — replace with actual data
Yellow fill | Field requires a data source — currently unsourced
Black text | Formula or calculated field — do not overwrite directly
Green text | Linked from another sheet in this workbook
Sheet Index
# | Sheet Name | Domain | Feeds Dashboard Tab | Suggested Data Source System | Update Frequency
1 | 01_Transformers | Power transformer master + live sensor fields | Grid Monitor / Overview | SCADA historian, DGA lab, asset register | Real-time / Daily
2 | 02_Lines_DLR | Transmission line master + DLR sensor fields | Grid Monitor / Overview | SCADA, DLR sensor vendor (e.g. Ampacimon, Lindsey), GIS | Real-time / Hourly
3 | 03_Towers_Drone | Transmission tower master + drone inspection log | Grid Monitor | Drone inspection vendor reports, GIS, O&M records | Per inspection cycle
4 | 04_STATCOM_Substations | STATCOM & substation master data | Grid Monitor / Overview | SCADA, substation asset register | Real-time / Daily
5 | 05_SCADA_System | Grid frequency, generation, load, reserves | Grid Monitor / Overview | SLDC SCADA/EMS system | Real-time (15-min blocks)
6 | 06_PowerPurchase | Source-wise power purchase mix & cost FY | Commercial | KPCL billing, PPAs, IEX/PXIL exchange records | Monthly
7 | 07_SalesMix | Consumer category sales, tariff, revenue | Commercial | ESCOM billing systems (e.g. Oracle CC&B), tariff orders | Monthly
8 | 08_Subsidy | GoK/GoI subsidy schemes & burden | Commercial / EHS | Energy Dept GoK budget docs, ESCOM subsidy claims | Quarterly
9 | 09_OpenAccess | Open access volumes & revenue impact | Commercial | ESCOM OA cell records, KERC OA approvals | Quarterly
10 | 10_ESCOM_Reliability | SAIDI/SAIFI/AT&C/DT failure by ESCOM | Reliability | ESCOM MIS, CEA reliability reports, RDSS portal | Monthly/Quarterly
11 | 11_Network_Assets | Substations, feeders, DTs, line km by ESCOM | Reliability | ESCOM asset GIS, annual reports | Annual / on change
12 | 12_GFA_Debt | Gross fixed assets & debt by ESCOM/KPTCL | Reliability | Audited financial statements, KERC tariff filings | Annual
13 | 13_ThermalStations | Thermal generating station performance | Reliability / EHS | KPCL generation MIS, CEA PLF reports | Monthly
14 | 14_EHS_Monitoring | EHS hazard register — arc flash, SF6, vegetation etc. | EHS & Carbon | Safety audits, SF6 gas monitoring system, LiDAR survey | Per audit / continuous
15 | 15_Carbon_Credits | Carbon intensity & credit potential levers | EHS & Carbon | CEA CO2 baseline database, BEE PAT scheme, internal loss studies | Annual
16 | 16_Incidents | Incident / fault log with MTTR tracking | Incidents | SCADA alarm log, O&M trouble ticketing system | Real-time
17 | 17_Maintenance | Maintenance schedule & work orders | Grid Monitor | CMMS / SAP PM module | Real-time
18 | 18_Outage_Impact | N-1 contingency / outage cascade simulation refs | Incidents | SLDC contingency analysis, planning studies | Annual / on network change

## 01_Transformers
Power Transformers — Master & Sensor Data
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Transformer ID | Name | Substation | Latitude | Longitude | Capacity (MVA) | Voltage Primary (kV) | Voltage Secondary (kV) | Commissioning Year | Make/OEM | Current Load % | Oil Temp °C (live) | Health Status | Data Source
TX-001 | Hebbal 220/66kV T1 | Hebbal | 13.035 | 77.597 | 160 | 220 | 66 |  |  | normal |  | Normal
TX-002 | Yeshwanthpur 220/66kV T2 | Yeshwanthpur | 13.0237 | 77.549 | 160 | 220 | 66 |  |  | normal |  | Normal
TX-003 | Whitefield 66/11kV T1 | Whitefield | 12.9698 | 77.75 | 40 | 66 | 11 |  |  | warning |  | Watch
TX-004 | Jayanagar 66/11kV T3 | Jayanagar | 12.9308 | 77.5931 | 40 | 66 | 11 |  |  | normal |  | Normal
TX-005 | Bellary Rd 400/220kV AT1 | Bellary Road | 13.0627 | 77.594 | 315 | 400 | 220 |  |  | critical |  | Critical
Live Sensor Field Reference (per reading, time-series)
Field | Unit | Description | Alert Threshold | Source System
load_pct | % | Transformer loading as % of rated MVA | >90% critical, >75% warning | SCADA / RTU
load_mva | MVA | Actual loading | — | SCADA / RTU
oil_t | °C | Top oil temperature | >75°C warning | RTD sensor / SCADA
wind_t | °C | Winding hotspot temperature | >90°C warning | RTD sensor / SCADA
pf | — | Power factor | <0.90 warning | SCADA
tap | position | OLTC tap position | — | SCADA
h2 | ppm | DGA — Hydrogen | >150 ppm IEC caution | Online DGA monitor / lab sample
c2h2 | ppm | DGA — Acetylene | >5 ppm critical (arcing indicator) | Online DGA monitor / lab sample
co | ppm | DGA — Carbon monoxide | Trend-based | Online DGA monitor / lab sample

## 02_Lines_DLR
Transmission Lines — Master & Dynamic Line Rating Data
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Line ID | Name | Voltage (kV) | Length (km) | Static Rating (MVA) | From Substation | To Substation | Conductor Type | Commissioning Year | Current Load % | Data Source
LN-001 | Hebbal–Whitefield 220kV | 220 | 22.4 | 320 | Hebbal | Whitefield |  |  | normal
LN-002 | Yeshwanthpur–Jayanagar 66kV | 66 | 11.8 | 80 | Yeshwanthpur | Jayanagar |  |  | overloaded
LN-003 | Bellary Rd–Hebbal 400kV | 400 | 8.2 | 630 | Bellary Road | Hebbal |  |  | normal
DLR Sensor Field Reference (per reading, time-series)
Field | Unit | Description | Alert Threshold | Source System
wind | m/s | Wind speed at conductor (weather station / DLR sensor) | — | DLR vendor sensor / weather API
dlr | MVA | Dynamic line rating computed from real-time weather | — | DLR engine (e.g. Ampacimon, CAT-1)
hdroom | % | Headroom = (DLR − actual load) / DLR | <10% critical, <20% warning | Calculated
cT | °C | Conductor temperature | >75°C warning | DLR sensor / sag-tension monitor
sag | m | Conductor sag | >12 m warning (clearance risk) | DLR sensor / LiDAR
pct | % | Loading as % of static rating | >100% critical, >85% warning | SCADA

## 03_Towers_Drone
Transmission Towers — Master & Drone Inspection Log
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Tower ID | Name | Line | Latitude | Longitude | Tower Type | Height (m) | Last Inspection Date | Status | Data Source
TW-100 | HBL-WFD-1 | Hebbal-Whitefield 220kV | 13.035 | 77.597 | Lattice | 35 | 2025-04-10 | normal
TW-101 | HBL-WFD-2 | Hebbal-Whitefield 220kV | 13.027 | 77.625 | Lattice | 35 | 2025-04-10 | normal
TW-102 | HBL-WFD-3 | Hebbal-Whitefield 220kV | 13.01 | 77.658 | Lattice | 35 | 2026-06-28 | drone_inspection
TW-103 | HBL-WFD-4 | Hebbal-Whitefield 220kV | 12.99 | 77.69 | Lattice | 35 | 2025-05-15 | normal
TW-104 | HBL-WFD-5 | Hebbal-Whitefield 220kV | 12.9698 | 77.75 | Lattice | 35 | 2025-05-15 | normal
TW-200 | YSP-JNR-1 | Yeshwanthpur-Jayanagar 66kV | 13.0237 | 77.549 | Monopole | 28 | 2025-03-20 | normal
TW-201 | YSP-JNR-2 | Yeshwanthpur-Jayanagar 66kV | 12.99 | 77.56 | Monopole | 28 | 2025-01-05 | anomaly
TW-202 | YSP-JNR-3 | Yeshwanthpur-Jayanagar 66kV | 12.96 | 77.575 | Monopole | 28 | 2025-03-20 | normal
TW-203 | YSP-JNR-4 | Yeshwanthpur-Jayanagar 66kV | 12.9308 | 77.5931 | Monopole | 28 | 2025-03-20 | normal
Drone Inspection Field Reference (per inspection cycle)
Field | Unit | Description | Alert Threshold | Source System
corr | % | Corrosion index from visual/thermal imagery | >10% critical, >5% warning | Drone vendor analytics (e.g. Skydio, Percepto)
sagD | % | Conductor sag deviation vs design | >8% warning | LiDAR survey via drone
insul | % | Insulator integrity score | <75% critical, <88% warning | Thermal/UV imagery AI scoring
veg | m | Vegetation clearance from conductor | <3.0 m action (CERC norm) | LiDAR vegetation encroachment survey
anomalies | list | Detected defects (strand break, pollution, hotspot) | Any 'break' = critical | AI defect detection model output

## 04_STATCOM_Substations
STATCOM & Substation Master Data
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
STATCOM Units
Unit ID | Name | Substation | Rating (±MVAR) | Latitude | Longitude | Commissioning Year | Status | Data Source
STC-001 | Hebbal STATCOM | Hebbal | 100 | 13.0355 | 77.5975 |  | active
STC-002 | Whitefield STATCOM | Whitefield | 50 | 12.9702 | 77.7505 |  | active
Substations
Substation ID | Name | Latitude | Longitude | Voltage Levels (kV) | SCADA Connected (Y/N) | Status | Data Source
SS-001 | Hebbal EHV Substation | 13.035 | 77.597 | 220/66 | Y | normal
SS-002 | Yeshwanthpur EHV Substation | 13.0237 | 77.549 | 220/66 | Y | normal
SS-003 | Whitefield HV Substation | 12.9698 | 77.75 | 66/11 | Y | warning
SS-004 | Jayanagar HV Substation | 12.9308 | 77.5931 | 66/11 | Y | normal
SS-005 | Bellary Road UHV Substation | 13.0627 | 77.594 | 400/220 | Y | critical

## 05_SCADA_System
SCADA / SLDC System-Level Data
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Field | Unit | Description | Current Value (placeholder) | Alert Threshold | Source System
freq | Hz | Grid frequency | 50 | ±0.05 Hz from 50.0 | SLDC EMS/SCADA
gen | MW | Total state generation | 2800 | — | SLDC EMS
load | MW | Total state demand | 2650 | — | SLDC EMS
vpu | p.u. | System voltage (per unit) | 1 | ±0.02 pu | SCADA
react_reserve | MVAR | Reactive power reserve available | 170 | <100 MVAR warning | SLDC EMS
spin_reserve | MW | Spinning reserve margin | 250 | <150 MW warning | SLDC EMS
alarms | count | Active SCADA alarms | 5 | >6 critical, >3 warning | SCADA alarm log
Note: For historical time-series, replicate this table per 15-minute SCADA block with a Timestamp column, or link directly to your EMS historian export.

## 06_PowerPurchase
Power Purchase Mix — Source-wise Cost Analysis
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
# | Source | Fiscal Year | MU (Million Units) | Rate (₹/kWh) | Cost (₹ Cr) | Type (Intra/Inter-state) | Data Source
1 | KPCL Hydro | FY25 | 10480 | 1.42 | 1394 | Intra
2 | KPCL Thermal | FY25 | 8960 | 5.28 | 4650 | Intra
3 | KPCL Gas | FY25 | 1100 | 6.84 | 807 | Intra
4 | CGS NTPC/NPCIL | FY25 | 7200 | 4.02 | 2822 | ISTS
5 | Solar PPAs | FY25 | 15200 | 3.24 | 4484 | Intra
6 | Wind PPAs | FY25 | 8640 | 3.84 | 3164 | Intra
7 | IPP Conventional | FY25 | 3980 | 5.82 | 2398 | Intra
8 | IEX / Exchange | FY25 | 4680 | 6.42 | 2748 | Inter
9 | Bilateral LT PPAs | FY25 | 2380 | 4.92 | 1102 | Inter
| TOTAL / APPC |  | 62620 | 3.7638 | 23569
Add additional fiscal years below by copying the block above with a new 'Fiscal Year' tag (e.g. FY24, FY23) to build the historical trend.
Note on E14: APPC = Total Cost(₹Cr)*10 / Total MU — verify formula vs KERC convention

## 07_SalesMix
Sales Mix by Consumer Category — BESCOM (template for all ESCOMs)
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
ESCOM: | BESCOM
Consumer Category | Fiscal Year | MU | % of Total | Tariff (₹/kWh) | Revenue (₹ Cr) | Subsidy Flag | Data Source
Residential BPL | FY25 | 1842 | 15.85% | 1.2 | 221 | GoK Gruha Jyothi
Residential General | FY25 | 3280 | 28.22% | 4.84 | 1587 | —
Residential HI | FY25 | 1420 | 12.22% | 8.24 | 1170 | —
LT Commercial | FY25 | 1280 | 11.01% | 8.64 | 1106 | —
Agriculture IP | FY25 | 2140 | 18.41% | 0 | 0 | GoK Free Power
LT Industrial | FY25 | 420 | 3.614% | 7.84 | 329 | —
HT Industrial | FY25 | 1240 | 10.67% | 7.42 | 920 | Open Access risk
TOTAL |  | 11622 | 100% |  | 5333

## 08_Subsidy
Subsidy Burden — GoK / GoI Schemes
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Scheme | Beneficiary | Fiscal Year | Amount (₹ Cr) | Budget Next FY (₹ Cr) | Risk Flag | Data Source
Gruha Jyothi (free 200u) | All Residential BPL | FY25 | 16021 | 17800 | Largest scheme
IP Free Power (Agri) | Farmers <10HP | FY25 | 9240 | 10200 | Unmetered consumption
RDSS Grant (GoI) | All ESCOMs Infra | FY25 | 3640 | 4200 | CapEx, conditional
PMSGY (GoI) | Rural ESCOMs | FY25 | 980 | 1100 | CapEx
Green Energy Corridor | KPTCL RE evacuation | FY25 | 284 | 320 | CapEx + VGF
BPL Tariff Subsidy | BPL consumers | FY25 | 1480 | 1680 | Arrears risk

## 09_OpenAccess
Open Access — Volumes & Revenue Impact Trend
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Fiscal Year | Open Access Volume (MU) | Revenue Lost (₹ Cr) | HT Industrial Migration Risk | Data Source
FY22-23 | 1840 | 2840 | Low
FY23-24 | 2280 | 3420 | Medium
FY24-25 | 2840 | 4180 | Medium-High
FY25-26 (Projected) | 3480 | 5120 | High

## 10_ESCOM_Reliability
ESCOM Reliability Indices vs CEA Norms
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
ESCOM | Fiscal Year | SAIDI (hrs/yr) | SAIFI (int/yr) | CAIDI (hrs) | AT&C Loss (%) | Smart Meter Coverage (%) | DT Failure Rate (%) | Data Source
BESCOM | FY25 | 8.2 | 12.4 | 0.66 | 12.8 | 8.4 | 2.4
MESCOM | FY25 | 18.6 | 22.8 | 0.82 | 16.4 | 3.2 | 3.2
HESCOM | FY25 | 28.4 | 34.2 | 0.83 | 21.2 | 2.8 | 4.1
GESCOM | FY25 | 32.8 | 40.6 | 0.81 | 24.8 | 2.4 | 5.2
CESC | FY25 | 22.4 | 28.8 | 0.78 | 18.6 | 4.2 | 3.8
CEA Target | — | 12 | 20 | 0.6 | 15 | — | 2 | CEA RDSS guideline
APSPDCL Best (peer ref) | FY25 | 10.2 | 14.8 | 0.69 | 9.8 | 18 | 1.8 | APSPDCL annual report (verify)

## 11_Network_Assets
Network Assets — HT:LT Ratio & Infrastructure by ESCOM
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
ESCOM | Fiscal Year | HT:LT Ratio | 33kV Substations | 33kV Line (km) | 11kV Feeders | Distribution Transformers | LT Line (km) | Data Source
BESCOM | FY25 | 1.28 | 442 | 8842 | 4280 | 148400 | 62800
MESCOM | FY25 | 0.94 | 248 | 4280 | 1840 | 68200 | 38400
HESCOM | FY25 | 0.82 | 312 | 6480 | 2180 | 84800 | 52400
GESCOM | FY25 | 0.76 | 284 | 5640 | 1920 | 72400 | 46800
CESC | FY25 | 1.02 | 194 | 3840 | 1480 | 58200 | 32200
CEA Ideal | — | 1.5 | — | — | — | — | — | CEA RDSS guideline

## 12_GFA_Debt
Gross Fixed Assets & Debt Profile — ESCOMs and KPTCL
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Entity | Fiscal Year | GFA (₹ Cr) | Debt (₹ Cr) | Data Source
BESCOM | FY25 | 42800 | 18240
MESCOM | FY25 | 14200 | 4280
HESCOM | FY25 | 18400 | 8240
GESCOM | FY25 | 15800 | 5640
CESC | FY25 | 12400 | 3840
KPTCL | FY25 | 28400 | 12480

## 13_ThermalStations
Thermal Generating Stations — Performance & Coal Security
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Station | Fiscal Year | Installed Capacity (MW) | PLF (%) | Coal Grade | GCV (kcal/kg) | Station Heat Rate (kcal/kWh) | Coal Stock (days) | Generation Cost (₹/kWh) | Data Source
RTPS Raichur Stage 1-7 | FY25 | 1740 | 62.4 | E/F | 3800 | 2780 | 18 | 3.82
BTPS Bellary Stage 1-3 | FY25 | 1700 | 68.2 | E | 3900 | 2720 | 11 | 3.74
YTPS Yermarus Stage 1-2 | FY25 | 800 | 71.8 | E | 3950 | 2680 | 8 | 3.68
UPCL Udupi (IPP) | FY25 | 1200 | 74.2 | Imported | 5800 | 2220 | 6 | 4.92

## 14_EHS_Monitoring
EHS Hazard Register — Substations, Lines & Towers
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Asset | Hazard Type | Description | Measured Value | Threshold/Standard | Risk Level | Last Assessed | Data Source
Bellary Rd 400kV | Arc Flash | Incident energy at switchgear | 48 cal/cm² | PPE Cat 4 / IEEE 1584 | High
Whitefield GIS | SF6 Leak | Gas pressure / leak rate | 4.8 bar (nom 5.2), 0.8%/yr | Leak threshold 1%/yr | Monitor
Tower YSP-JNR-2 | Vegetation | Clearance from conductor | 1.8 m | CERC min 3.0 m | Action
Hebbal T1 | Oil Containment | Bund capacity vs oil volume | 110% of transformer oil volume | CPCB norm 110% | OK
Jayanagar SS | Earthing | Earth resistance | 0.28 Ω | IS 3043 limit 1.0 Ω | OK
Hebbal 220kV Corridor | EMF | Field strength at corridor edge | 12 kV/m | ICNIRP public limit 10 kV/m | Review
RTPS Transformers | PCB Oil | PCB content compliance check | Last sample FY24 | CPCB compliance schedule | Due
Jayanagar Substation | Noise | Ambient noise level | 84 dBA | CPCB industrial limit 75 dBA | Action

## 15_Carbon_Credits
Carbon Intensity & Carbon Credit Potential
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Grid Emission Factor | 0.82 | kg CO2 / kWh — Source: CEA CO2 Baseline Database (verify latest version)
Fuel Mix FY25 (%)
Source | Share (%) | Data Source
Solar | 19
Wind | 13.4
Hydro | 5.9
Thermal | 19.7
Gas | 3.4
Other (CGS/IPP/Exchange) | 38.6
Carbon Credit Levers
Lever | Loss Reduction (%) | tCO2/yr Saved | Credits (₹ Cr/yr) | Data Source
DLR Deployment | 0.4 | 18400 | 19.2
STATCOM reactive optimisation | 0.2 | 9200 | 9.6
Smart Metering AT&C reduction | 1.2 | 55200 | 57.8
RE curtailment reduction | 0.6 | 27600 | 28.9
Total Potential | 2.4 | 110400 | 115.5

## 16_Incidents
Incident / Fault Log
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Incident ID | Asset | Description | Severity | Opened (Date/Time) | Closed (Date/Time) | Assigned To | Status
INC-001 | TX-005 | Overload 94.2% · DGA C2H2 12.4 ppm elevated | P1 Critical |  |  | EE Bellary Circle | Open
INC-002 | LN-002 | Line overloaded 103.2% of static rating | P1 Critical |  |  | SE Operations SLDC | Open
INC-003 | TW-201 | Conductor strand break (Drone confirmed) | P1 Critical |  |  | Line Gang 4 | Open
INC-004 | TX-003 | Oil temp 78.4°C, cooling fans tripped | P2 Warning |  |  | AEE Whitefield SS | In Progress
INC-005 | TW-102 | Drone inspection underway | P2 Warning |  |  | Drone Team Alpha | In Progress
INC-006 | LN-001 | DLR headroom <10% — wind speed dropped | P2 Warning |  |  | SLDC Control Room | In Progress
INC-007 | STC-001 | Capacitor bank trip — restored | P3 Resolved |  |  | EE Maintenance | Closed
INC-008 | BESCOM Fdr-14 | 33kV feeder fault — auto-reclosed | P3 Resolved |  |  | Auto-reclose | Closed
MTTR Calculation
MTTR (avg, hrs) | 2.4 | MTTR = AVERAGE(Closed Time minus Opened Time) across all closed incidents in period

## 17_Maintenance
Maintenance Schedule & Work Orders
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Asset ID | Task Description | Due Date | Priority | Status | Assigned Team
TX-005 | Emergency DGA + oil sample |  | P1 | Open
TX-003 | Thermal scan + load shed |  | P2 | Scheduled
TW-201 | Line gang — strand repair |  | P1 | In Progress
LN-002 | Load transfer to LN-001 |  | P2 | Review
TW-102 | Drone visual inspection |  | P2 | Active
TX-001 | Annual scheduled maintenance |  | P3 | Planned

## 18_Outage_Impact
N-1 Contingency / Outage Impact Simulation Reference
Cells highlighted YELLOW need a data source / actual figure filled in. BLUE text = current placeholder value (replace with real data). Add 'Source' column entries as: System/Document, Date, Reference.
Asset | If Trips... | MW Affected | ESCOMs Impacted | Cascade Risk | Mitigation Action
TX-005 | Bellary Rd AT1 trips | 315 | BESCOM + HESCOM | Critical | Manual redispatch
LN-001 | Hebbal–Whitefield 220kV trips | 280 | BESCOM North | High | Switch to LN-003
LN-002 | YSP–Jayanagar 66kV trips | 72 | BESCOM South | Medium | Load shed 72 MW
STC-001 | Hebbal STATCOM trips | — | Voltage stability | Medium | STC-002 ramp up
Note: These should be derived from your SLDC's N-1 contingency analysis / load flow studies, re-validated whenever network topology changes.